## Sheet1
From manual | Lookup Value | Register ID | Description | Writable
40001 Process Value (PV) N/A N/A N/A Read Only 1 = 1 Display unit | 40001 | 0 | Process Value (PV) | FALSE | 0: '40001 = Process Value (PV)',
40002 Active Setpoint (SP) -999 9999 0 Read/Write 1 = 1 Display unit | 40002 | 1 | Active Setpoint (SP) | TRUE | 1: '40002 = Active Setpoint (SP)',
40003 Setpoint 1 (SP1) -999 9999 0 Read/Write 1 = 1 Display unit | 40003 | 2 | Setpoint 1 (SP1) | TRUE | 2: '40003 = Setpoint 1 (SP1)',
40004 Setpoint 2 (SP2) -999 9999 0 Read/Write 1 = 1 Display unit | 40004 | 3 | Setpoint 2 (SP2) | TRUE | 3: '40004 = Setpoint 2 (SP2)',
40005 Setpoint Deviation N/A N/A N/A Read Only 1 = 1 Display unit | 40005 | 4 | Setpoint Deviation | FALSE | 4: '40005 = Setpoint Deviation',
40006 Alarm 1 Value -999 9999 100 Read/Write 1 = 1 Display unit | 40006 | 5 | Alarm 1 Value | TRUE | 5: '40006 = Alarm 1 Value',
40007 Alarm 2 Value -999 9999 200 Read/Write 1 = 1 Display unit | 40007 | 6 | Alarm 2 Value | TRUE | 6: '40007 = Alarm 2 Value',
40008 Alarm 3 Value -999 9999 300 Read/Write 1 = 1 Display unit | 40008 | 7 | Alarm 3 Value | TRUE | 7: '40008 = Alarm 3 Value',
40009 Output Power 1 0 1000 0 Read/Write 1 = 0.1%; writable when in manual mode only. | 40009 | 8 | Output Power 1 | TRUE | 8: '40009 = Output Power 1',
40010 Output Power 2 0 1000 0 Read/Write 1 = 0.1%; writable when in manual mode only. | 40010 | 9 | Output Power 2 | TRUE | 9: '40010 = Output Power 2',
40011 PB Proportional band (Active) 1 999(.9)° or 9999 (process) 70 Read/Write 1 = 1 Display unit | 40011 | 10 | PB Proportional band (Active) | TRUE | 10: '40011 = PB Proportional band (Active)',
40012 Integral time (Active) 0 9999 120 Read/Write 1 = 1 second | 40012 | 11 | Integral time (Active) | TRUE | 11: '40012 = Integral time (Active)',
40013 Derivative time (Active) 0 9999 30 Read/Write 1 = 1 second | 40013 | 12 | Derivative time (Active) | TRUE | 12: '40013 = Derivative time (Active)',
40014 Integration default (Active) 0 1000 0 Read/Write 1 = 0.1 % output power | 40014 | 13 | Integration default (Active) | TRUE | 13: '40014 = Integration default (Active)',
40015 PID parameter set selection 0 1 0 Read/Write 0 = PID Set 1, 1 = PID Set 2 | 40015 | 14 | PID parameter set selection | TRUE | 14: '40015 = PID parameter set selection',
40016 Auto-Tune Start 0 1 0 Read/Write 0 = No; 1 = Yes | 40016 | 15 | Auto-Tune Start | TRUE | 15: '40016 = Auto-Tune Start',
40017 Control Mode Transfer (Auto/Manual) 0 1 0 Read/Write 0 = Automatic (PID), 1 = User (Manual Mode) | 40017 | 16 | Control Mode Transfer (Auto/Manual) | TRUE | 16: '40017 = Control Mode Transfer (Auto/Manual)',
40018 Controller Status 0 1 1 Read/Write 0: Stop, 1: Run | 40018 | 17 | Controller Status | TRUE | 17: '40018 = Controller Status',
40019 Setpoint Select 0 1 0 Read/Write 0 = SP1, 1 = SP2 | 40019 | 18 | Setpoint Select | TRUE | 18: '40019 = Setpoint Select',
40020 SP Ramp Rate 0 999(.9)° or 9999 (process) 0 Read/Write 1 = 1 Display unit/minute; 0 = Ramping disabled | 40020 | 19 | SP Ramp Rate | TRUE | 19: '40020 = SP Ramp Rate',
40021 LED Status N/A N/A N/A Read Only Bit State: 0 = Off, 1 = On b7: AT, b6:OUT1, b5: OUT2, b4: ALM1, b3: °C, b2: °F, b1: ALM2, b0: ALM3 | 40021 | 20 | LED Status | FALSE | 20: '40021 = LED Status',
40022 Pushbutton Status N/A N/A N/A Read Only Bit State: 0 = Key pressed, 1 = Key not pressed b7: D, b6: Up, b5: F1, b4: N/A, b3: P, b2: Down, b1: F2, b0: N/A | 40022 | 21 | Pushbutton Status | FALSE | 21: '40022 = Pushbutton Status',
40023 Alarm Reset 0 7 0 Read/Write Bit State: 1 = reset alarm, bit is returned to zero following reset b3: Reset Alm3, b1: Reset Alm2, b0: Reset Alm1 | 40023 | 22 | Alarm Reset | TRUE | 22: '40023 = Alarm Reset',
40024 Setpoint Ramping Disable 0 1 0 Read/Write 0 = Enabled, 1 = Disabled | 40024 | 23 | Setpoint Ramping Disable | TRUE | 23: '40024 = Setpoint Ramping Disable',
40025 Integral Action Disable 0 1 0 Read/Write 0 = Enabled, 1 = Disabled PID PARAMETERS | 40025 | 24 | Integral Action Disable | TRUE | 24: '40025 = Integral Action Disable',
40033 Proportional band 1 1 999(.9)° or 9999 (process) 70 Read/Write 1 = 1 Display unit | 40033 | 32 | Proportional band | TRUE | 32: '40033 = Proportional band',
40034 Integral time 1 0 9999 120 Read/Write 1 = 1 second | 40034 | 33 | Integral time | TRUE | 33: '40034 = Integral time ',
40035 Derivative time 1 0 9999 30 Read/Write 1 = 1 second | 40035 | 34 | Derivative time | TRUE | 34: '40035 = Derivative time',
40036 Integration default 1 0 1000 0 Read/Write 1 = 0.1 % | 40036 | 35 | Integration default | TRUE | 35: '40036 = Integration default',
40037 Proportional band 2 1 999(.9)° or 9999 (process) 70 Read/Write 1 = 1 Display unit | 40037 | 36 | Proportional band | TRUE | 36: '40037 = Proportional band',
40038 Integral time 2 0 9999 120 Read/Write 1 = 1 second | 40038 | 37 | Integral time 2 | TRUE | 37: '40038 = Integral time 2',
40039 Derivative time 2 0 9999 30 Read/Write 1 = 1 second | 40039 | 38 | Derivative time 2 | TRUE | 38: '40039 = Derivative time 2',
40040 Integration default 2 0 1000 0 Read/Write 1 = 0.1 % | 40040 | 39 | Integration default 2 | TRUE | 39: '40040 = Integration default 2',
40041 Output Power Offset 0 1000 500 Read/Write 1 = 0.1 % output power INPUT PARAMETERS | 40041 | 40 | Output Power Offset | TRUE | 40: '40041 = Output Power Offset',
40051 Input Type 0 19 1 Read/Write 0 = tc-K 1 = tc-J 2 = tc-t 3 = tc-E 4 = tc-N 5 = tc-r 6 = tc-S 7 = tc-b 8 = tc-L 9 = tc-U 10 = tc-txk 11 = r392 12 = r385 13 = n114 = cu50 15 = 5v 16 = 10v 17 = 0-20mA 18 = 4-20mA 19 = 0.05v | 40051 | 50 | Input Type | TRUE | 50: '40051 = Input Type',
40052 Temperature Scale 0 1 0 Read/Write 0 = °F, 1 = °C | 40052 | 51 | Temperature Scale | TRUE | 51: '40052 = Temperature Scale',
40053 Decimal Resolution 0 3 0 Read/Write0 = 0 (No decimal place) 1 = 0.0, 2 = 0.00, 3 = 0.000. Temperature inputs are limited to 1 decimal point except for the thermocouple B,S,R types, which display in whole units only (0) | 40053 | 52 | Decimal Resolution | TRUE | 52: '40053 = Decimal Resolution',
40054 Digital Filtering 0 50 8 Read/Write 0 = least, 50 = most | 40054 | 53 | Digital Filtering | TRUE | 53: '40054 = Digital Filtering',
40055 Input Filter Band 0 25(.0)° or 250 (process) 1 Read/Write 1 = 1 Display unit | 40055 | 54 | Input Filter Band | TRUE | 54: '40055 = Input Filter Band',
40056 Shift/Offset -99(.9)° or 999 (process)99(.9)° or 999 (process) 0 Read/Write 1 = 1 Display unit | 40056 | 55 | Shift/Offset | TRUE | 55: '40056 = Shift/Offset',
40057 Display Value Scaling Point 1 -999 9999 0 Read/Write 1 = 1 Display unit; Value associated with lower range of input signal (0V, 0mA or 4mA) | 40057 | 56 | Display Value Scaling Point 1 | TRUE | 56: '40057 = Display Value Scaling Point 1',
40058 Display Value Scaling Point 2 -999 9999 1000 Read/Write 1 = 1 Display unit; Value associated with upper limit of input signal (50mV, 5V, 10V, or 20mA) | 40058 | 57 | Display Value Scaling Point 2 | TRUE | 57: '40058 = Display Value Scaling Point 2',
40059 Setpoint Low Limit depending on sensor type Upper-limit of temperature range -148 Read/Write 1 = 1 Display unit | 40059 | 58 | Setpoint Low Limit | TRUE | 58: '40059 = Setpoint Low Limit',
40060 Setpoint High Limit Lower-limit of temperature range Depends on sensor type 2192 Read/Write 1 = 1 Display unit | 40060 | 59 | Setpoint High Limit | TRUE | 59: '40060 = Setpoint High Limit',
40061 Cold Junction Compensation 0 1 0 Read/Write 0 = ON, 1 = OFF | 40061 | 60 | Cold Junction Compensation | TRUE | 60: '40061 = Cold Junction Compensation',
40062 User Input 1 Function 0 9 or 10 0 Read/Write 0 = NONE, 1 = Run/Stop, 2 = Setpoint 1/2 select, 3 = Auto/Manual control, 4 = PLOC, 5 = Integral Lock, 6 = SP Ramp Disable, 7 = Reset Alarms, 8 = Rst Alm1, 9 = Rst Alm2, 10 = Rst Alm3 | 40062 | 61 | User Input 1 Function | TRUE | 61: '40062 = User Input 1 Function',
40063 User Input 2 Function 0 9 or 10 0 Read/Write 0 = NONE, 1 = Run/Stop, 2 = Setpoint 1/2 select, 3 = Auto/Manual control, 4 = PLOC, 5 = Integral Lock, 6 = SP Ramp Disable, 7 = Reset Alarms, 8 = Rst Alm1, 9 = Rst Alm2, 10 = Rst Alm3 | 40063 | 62 | User Input 2 Function | TRUE | 62: '40063 = User Input 2 Function',
40064 F1 Key Function 0 6 or 7 0 Read/Write 0 = NONE, 1 = Run/Stop, 2 = Setpoint 1/2 select, 3 = Auto/Manual control, 4 = Reset Alarms, 5 = Rst Alm1 , 6 = Rst Alm2 , 7 = Rst Alm3 | 40064 | 63 | F1 Key Function | TRUE | 63: '40064 = F1 Key Function',
40065 F2 Key Function 0 6 or 7 0 Read/Write 0 = NONE, 1 = Run/Stop, 2 = Setpoint 1/2 select, 3 = Auto/Manual control, 4 = Reset Alarms, 5 = Rst Alm1 , 6 = Rst Alm2 , 7 = Rst Alm3 | 40065 | 64 | F2 Key Function | TRUE | 64: '40065 = F2 Key Function',
40081 Output Action 0 1 or 5 0 Read/Write Single Output Model: 0 = r1, 1 = d1; Dual Output Model: 0 = r1r2, 1 = d1r2, 2 = r1d2, 3 = d1d2, 4 = r1A2, 5 = d1A2 r = reverse acting, d = direct acting, A = Alarm 3, numeric value indicates OP1 or OP2, | 40081 | 80 | Output Action | TRUE | 80: '40081 = Output Action',
40082 Auto Control Mode 0 1 0 Read/Write 0 = PID, 1 = On-Off | 40082 | 81 | Auto Control Mode | TRUE | 81: '40082 = Auto Control Mode',
40083 Output 1 Cycle Time 0 250 20 Read/Write 1 = 0.1 sec; A setting of zero will keep output off. | 40083 | 82 | Output 1 Cycle Time | TRUE | 82: '40083 = Output 1 Cycle Time',
40084 Output 1 Power Lower Limit 0 Output 1 Power High Limit 0 Read/Write 1 = 0.1 % | 40084 | 83 | Output 1 Power Lower Limit | TRUE | 83: '40084 = Output 1 Power Lower Limit',
40085 Output 1 Power High Limit Output 1 Power Lower Limit 1000 1000 Read/Write 1 = 0.1 % | 40085 | 84 | Output 1 Power High Limit | TRUE | 84: '40085 = Output 1 Power High Limit',
40086 Input Fail OP1 Power Level 0 1000 0 Read/Write 1 = 0.1 % | 40086 | 85 | Input Fail OP1 Power Level | TRUE | 85: '40086 = Input Fail OP1 Power Level',
40087 Analog Out 1 Low Scaling Value -999 9999 0 Read/Write 1 = 0.1 % | 40087 | 86 | Analog Out 1 Low Scaling | TRUE | 86: '40087 = Analog Out 1 Low Scaling',
40088 Analog Out 1 High Scaling Value -999 9999 1000 Read/Write 1 = 0.1 % | 40088 | 87 | Analog Out 1 High Scaling Value | TRUE | 87: '40088 = Analog Out 1 High Scaling Value',
40091 Output 2 Cycle Time 0 250 20 Read/Write 1 = 0.1 sec; A setting of zero will keep output off. | 40091 | 90 | Output 2 Cycle Time | TRUE | 90: '40091 = Output 2 Cycle Time',
40092 Output 2 Power Lower Limit 0 Output 2 Power High Limit 0 Read/Write 1 = 0.1 % | 40092 | 91 | Output 2 Power Lower Limit | TRUE | 91: '40092 = Output 2 Power Lower Limit',
40093 Output 2 Power High Limit Output 2 Power Lower Limit 1000 1000 Read/Write 1 = 0.1 % | 40093 | 92 | Output 2 Power High Limit | TRUE | 92: '40093 = Output 2 Power High Limit',
40094 Input Fail OP2 Power Level 0 1000 0 Read/Write 1 = 0.1 % | 40094 | 93 | Input Fail OP2 | TRUE | 93: '40094 = Input Fail OP2',
40095 Relative Gain 1 9999 100 Read/Write 1 = 0.01; In combination Reverse(r) and Direct(d) modes, this defines the gain of OP2 relative to OP1. | 40095 | 94 | Relative Gain | TRUE | 94: '40095 = Relative Gain',
40096 Deadband/Overlap -99(.9) or -999 (process) 999(.9)° or 9999 (process) 2 Read/Write 1 = 1 Display unit; In combination Reverse(r) and Direct(d) modes, this defines the overlap area in which both OP1 and OP2 are active (negative value) or the deadband area (positive value). | 40096 | 95 | Deadband/Overlap | TRUE | 95: '40096 = Deadband/Overlap',
40097 On/Off Control Hysteresis 2 250(.0)° or 2500 (process) 2 Read/Write 1 = 1 Display unit | 40097 | 96 | On/Off Control Hysteresis 2 | TRUE | 96: '40097 = On/Off Control Hysteresis 2',